## 20P03 pump
On 14-Jun-2016, identified that 20P03B pump was very unefficent pump.
Instead of running 20P03B, if we run P9002A/B we can saving hug power
Power consumption data was collected based on which 75 KW power saving was achieved.
|  | 20P03 B | P-9002 A |  | Power saving
Power consumption | KW | 142 | 67 |  | 75
Current | Amp | 221 | 126
Power factor |  | 0.87
Voltage | V | 425 | 365
Frequency | Hz |  | 44
|  | Power cost for calculation |  |  | 5
|  | Hourly saving |  | Rs/hr | 375
|  | Daily saving |  | Rs/day | 9000
Since 15 days per month, situation arise when we can save this much power
|  | hence monthly saving |  | Rs/month | 135000
|  | Annual saving |  | Rs/year | 1620000

## Heat exchangers analysis
Section 3 heat exchangers analysis
|  | Design data |  | 2016-06-08 |  | 2016-06-10 |  |  |  | After cleaning |  | Before cleaning
E-357 | Spiral | Cold Side | Hot Side | Cold Side | Hot Side | Cold Side | Hot Side | E-357 | Spiral | Cold Side | Hot Side | Cold Side | 102.4634 | 130.9028
Fluid |  | FA | FA | FA | FA | FA | FA | Fluid |  | FA | FA | Hot Side | 116 | 168.4
Flow | Kg/hr | 30000 | 18200 | 22000 | 13650 | 21700 | 13086 | Flow | Kg/hr | 22000 | 13650
Temp (in) | °C | 123.3 | 176 | 97.3698 | 164.5 | 102.4634 | 168.4 | Temp (in) | °C | 97.3698 | 164.5 | After cleaning
Temp (out) | °C | 153.4 | 128.6 | 125.1228 | 114.8 | 130.9028 | 116 | Temp (out) | °C | 132.7357 | 104.5 | Cold Side | 97.3698 | 132.7357
Cp | Kcal/Kg°C | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | Cp | Kcal/Kg°C | 0.6 | 0.6 | Hot Side | 104.5 | 164.5
Heat Load | Kcal/hr | 491727.6 | 517608 | 366338.7 | 407043 | 370281.456 | 411423.84 | Heat Load | Kcal/hr | 466830 | 491400
LMTD | °C | 11.929 |  | 26.9294 |  | 23.5168 |  | LMTD | °C | 16.4886 |  | 7.613
Area | m2 | 174 |  | 174 |  | 174 |  | Area | m2 | 174 |  | 118225.0588
HTC | Kcal/hrm2°C | 236.9027 |  | 78.182 |  | 90.4906 |  | HTC | Kcal/hrm2°C | 162.7143 |  | 1214641.0153 |  | 165.8319
| W/m2K | 275.0704 |  | 90.778 |  | 105.0697 |  |  | W/m2K | 188.9294
|  | Design data |  | 2016-06-08 |  | 2016-06-10 |  |  |  | After cleaning |  | Before cleaning
E-358 | Spiral | Cold Side | Hot Side | Cold Side | Hot Side | Cold Side | Hot Side | E-358 | Spiral | Cold Side | Hot Side | Cold Side | 130.9028 | 142.1013
Fluid |  | FA | FA | FA | FA | FA | FA | Fluid |  | FA | FA | Hot Side | 165.1 | 220.6
Flow | Kg/hr | 30000 | 9800 | 22000 | 6200 | 21700 | 4865 | Flow | Kg/hr | 22000 | 6200
Temp (in) | °C | 149.2 | 257 | 125.1228 | 225.1 | 130.9028 | 220.6 | Temp (in) | °C | 132.7357 | 225.1 | After cleaning
Temp (out) | °C | 179.9 | 165 | 139.4279 | 168.7 | 142.1013 | 165.1 | Temp (out) | °C | 154.7162 | 143 | Cold Side | 132.7357 | 154.7162
Cp | Kcal/Kg°C | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | Cp | Kcal/Kg°C | 0.6 | 0.6 | Hot Side | 143 | 225.1
Heat Load | Kcal/hr | 513912 | 540960 | 188827.2 | 209808 | 145804.05 | 162004.5 | Heat Load | Kcal/hr | 290141.4 | 305412
LMTD | °C | 38.6728 |  | 62.2712 |  | 53.315 |  | LMTD | °C | 31.2261 |  | 15.2883
Area | m2 | 45.3 |  | 45.3 |  | 45.3 |  | Area | m2 | 45.3 |  | 7.3883
HTC | Kcal/hrm2°C | 293.3492 |  | 66.939 |  | 60.3701 |  | HTC | Kcal/hrm2°C | 205.1129 |  | 114735.8824 |  | 205.3444
| W/m2K | 340.611 |  | 77.7236 |  | 70.0964 |  |  | W/m2K | 238.1589 |  | 1178793.3118
[8 empty] | rise in feed temp |  | 15.2883 | °C
[8 empty] | Energy saving |  | 237418.2353 | Kcal/hr
[8 empty] | Cost saving |  | 2439228.4448 | Lacs Rs/year

## VAM chilled water to GDP
Sr. No. | SH1
Project: | VAM chilled water to GDP
Project Owner: | Shrish
Potential Saving in Rs Lac: | 23.6988 | Estimated Expense in Rs Lac: | 6 | Net Saving in FY16-17 in Rs Lac : | 13.2741 |  |  |  | Actual data | Running KW
[8 empty] | Tag No. | Description | 2016-12-26
Base Data: | [7 empty] | P-7126A | SCRUBBER CIRCULATION PUMP | 2.51
Power consumption before modification | [7 empty] | P-7126B | SCRUBBER CIRCULATION PUMP | 8.94
Chiller A Power consumption |  |  | KW | 44 | Measured |  |  | P-7126C | SCRUBBER CIRCULATION PUMP | OFF
Chiller B Power consumption |  |  | KW | 44 | Measured |  |  | P-7126D | SCRUBBER CIRCULATION PUMP | 12.15
Chiller Pump- P-7126A Power consumption |  |  | KW | 8 | Measured |  |  | P-1013A | CHILLED WATER PUMP-A | 27.12
Chiller Pump- P-7126B Power consumption |  |  | KW | 2 | Measured |  |  | P-1013B | CHILLED WATER PUMP-B | OFF
Chiller Pump- P-7126D Power consumption |  |  | KW | 9 | Measured |  |  | P-1013C | CHILLED WATER PUMP-C | 27.12
Total present power consumption |  |  | KW | 107 | Calculated |  |  | CH-7000A | CHILLER-1 | 40.49
[8 empty] | CH-7000B | CHILLER-2 | 32.41
Power consumption after modification | [8 empty] | BOOSTER PUMP (B/W FLAKER AND CHP) | 19.84
Power consumption by booster pump |  |  | KW | 20 | Estimated
Net Power saving |  |  | KW | 87 | Calculated |  |  |  | Power consumption before modification | 96.5
Power Cost |  |  | Rs/KW | 5 |  |  |  |  | Power consumption after modification | 19.84
Total Running days per year |  |  | Days | 227 | Estimated |  |  |  | Power saving | 76.66
Net Saving |  |  | Rs/annum | 2369880 | Calculated
[9 empty] | Power cost | 5.8
Total saving |  |  | Rs/annum | 23.6988 | Calculated |  |  |  | Daily saving (Rs) | 10671.072
Run hr | [9 empty] | 76.55 | 432
Power cost | [9 empty] | 6.06 | 5.99
Saving per hr (base on actual KW data ) | [9 empty] | 76.66 | 76.66
| April | May | June | July | August | September | October | November | December | January | February | March
Saving achieved in Lac | [9 empty] | 0.35562 | 1.9837
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das

## VAM water to flaker
Sr. No. | DD1
Project: | FLAKER 24% increase production/day over present
Project Owner: | Dinesh Danav
Potential Saving in Rs Lac: | 10.6408 | Estimated Expense in Rs Lac: | 5 | Net Saving in FY16-17 in Rs Lac : | 4.2306
Base Data
Input Mat | Input Qty |  | Prod Days | Prodtn after increase 24% | 50 MT/day
Behenic Acid (Bulk) | 504 |  | 13.2632 | 10.08 | 10.08
Hyd LGMFA | 8151.2694 |  | 214.5071 | 163.0254 | 163.0254
Primestric - 12 Bulk | 1160 |  | 30.5263 | 23.2 | 23.2
Stearic 90 Bulk | 2460 |  | 64.7368 | 49.2 | 49.2
| 12275.2694 | 0 | 323.0334 | 245.5054 | 245.5054
|  | Days decreased |  | 77.528
|  | Power per MT | 30 |  | KWH
TOTAL power
|  | Power per day | 750 | 58147.5
|  |  |  | 319811.25 | RS.
OR
|  | Production reduced after 24% increas |  | 2946.0646
|  | Power per MT |  | 30
|  | Power reduced |  | 88381.9394
|  | Total cost |  | 486100.6669 | RS.
|  | Manpower reduction | 400 | 744268.9636 | Rs
|  | No of Man | 24
|  | No of Days | 77.528
|  | TOTAL SAVINGS |  | 1064080.2136 | RS
FLAKER (Manpower &Power)
| April | May | June | July | August | September | October | November | December | January | February | March | Total
Saving achieved in Lac | [7 empty] | 0.532 | 0.636 | 0.94 | 0.26 |  | 2.368
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das

## New TF condensate recovery
Sr. No. | PKD4
Project: | Condensate recovery in Tankfarm
Project Owner: | Prabhat Das
Potential Saving in Rs Lac: | 5.016 | Estimated Expense in Rs Lac: | 1.5 | Net Saving in FY16-17 in Rs Lac : | 2.344
*Recovery started from 1 Oct-2016
Base Data:
Improvement in condensate recovery after modification |  |  |  | 20 | m3/day
DM water cost saving |  |  |  | 860 | INR/day
ETP cost reduction |  |  |  | 660 | INR/day
Total saving per day |  |  |  | 1520 | INR/day
Annual saving (@330 days per year) |  |  |  | 501600 | INR/Year
| April | May | June | July | August | September | October | November | December | January | February | March | Total
Saving achieved in Lac | 0 | 0 | 0 | 0 | 0 | 0 | 0.42408 | 0.42 | 0.42 | 0.21 | 0 | 0.315 | 1.7891
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das